## Tag Master Data
Tag Name (M) | Tag Id (M) | Tag Description (M) | Plant (M) | Area (M) | Equipment (M) | Data Type (M) | Unit (M) | Alarm Enabled | Alarm High Limit | Alarm HH Limit | Alarm Low Limit | Alarm LL Limit | Alarm Priority | PLC IP Address | PLC Port | PLC Type | Sub Equipment | Component (M) | Logging Interval ms | Equipment Criticality | SIGNAL TYPE
PY1101A | PY1101A | FILTER INLET PRESSURE 1# | FTP-1 | POTLINE | DUCT | REAL | KPA | Yes | 1.5 |  | 0.7 |  |  | 192.168.1.11 |  | ControlLogix | DUCT INLET-1 | PRESSURE 1# |  | 3 | AI
PY1101B | PY1101B | FILTER INLET PRESSURE 2# | FTP-1 | POTLINE | DUCT | REAL | KPA | Yes | 1.5 |  | 0.7 |  |  | 192.168.1.11 |  | ControlLogix | DUCT INLET-2 | PRESSURE 2# |  | 3 | AI
PY1103A | PY1103A | ROOTS FAN OUTLET OF PRESSURE #1 | FTP-1 | POTLINE | BLOWER | REAL | KPA | Yes | 20.7 | 60 | 14.5 | 8 |  | 192.168.1.11 |  | ControlLogix | AIR ROOT BLOWER-1 | OUTLET PRESSURE #1 |  | 2 | AI
PY1103B | PY1103B | ROOTS FAN OUTLET OF PRESSURE #2 | FTP-1 | POTLINE | BLOWER | REAL | KPA | Yes | 20.7 | 60 | 14.5 | 8 |  | 192.168.1.11 |  | ControlLogix | AIR ROOT BLOWER-2 | OUTLET PRESSURE #2 |  | 2 | AI
PY1104 | PY1104 | CHUTE SILO FAN OUTLET OF PRESSURE | FTP-1 | POTLINE | FAN | REAL | KPA | Yes | 9 | 10 | 6 | 4 |  | 192.168.1.11 |  | ControlLogix | AIRSLIDE FAN | OUTLET PRESSURE |  | 2 | AI
PY1105A | PY1105A | FILTER AIR BAG OF PRESSURE #1 | FTP-1 | POTLINE | BAG HOUSE | REAL | KPA | Yes | 0.4 | 0.6 | 0.3 | 0.15 |  | 192.168.1.11 |  | ControlLogix | FILTER-1 | PRESSURE #1 |  | 2 | AI
PY1105B | PY1105B | FILTER AIR BAG OF PRESSURE #2 | FTP-1 | POTLINE | BAG HOUSE | REAL | KPA | Yes | 0.4 | 0.6 | 0.3 | 0.15 |  | 192.168.1.11 |  | ControlLogix | FILTER-2 | PRESSURE #2 |  | 2 | AI
PY1105C | PY1105C | FILTER AIR BAG OF PRESSURE #3 | FTP-1 | POTLINE | BAG HOUSE | REAL | KPA | Yes | 0.4 | 0.6 | 0.3 | 0.15 |  | 192.168.1.11 |  | ControlLogix | FILTER-3 | PRESSURE #3 |  | 2 | AI
PY1105D | PY1105D | FILTER AIR BAG OF PRESSURE #4 | FTP-1 | POTLINE | BAG HOUSE | REAL | KPA | Yes | 0.4 | 0.6 | 0.3 | 0.15 |  | 192.168.1.11 |  | ControlLogix | FILTER-4 | PRESSURE #4 |  | 2 | AI
PY1105E | PY1105E | FILTER AIR BAG OF PRESSURE #5 | FTP-1 | POTLINE | BAG HOUSE | REAL | KPA | Yes | 0.4 | 0.6 | 0.3 | 0.15 |  | 192.168.1.11 |  | ControlLogix | FILTER-5 | PRESSURE #5 |  | 2 | AI
PY1105F | PY1105F | FILTER AIR BAG OF PRESSURE #6 | FTP-1 | POTLINE | BAG HOUSE | REAL | KPA | Yes | 0.4 | 0.6 | 0.3 | 0.15 |  | 192.168.1.11 |  | ControlLogix | FILTER-6 | PRESSURE #6 |  | 2 | AI
PY1105G | PY1105G | FILTER AIR BAG OF PRESSURE #7 | FTP-1 | POTLINE | BAG HOUSE | REAL | KPA | Yes | 0.4 | 0.6 | 0.3 | 0.15 |  | 192.168.1.11 |  | ControlLogix | FILTER-7 | PRESSURE #7 |  | 2 | AI
PY1105H | PY1105H | FILTER AIR BAG OF PRESSURE #8 | FTP-1 | POTLINE | BAG HOUSE | REAL | KPA | Yes | 0.4 | 0.6 | 0.3 | 0.15 |  | 192.168.1.11 |  | ControlLogix | FILTER-8 | PRESSURE #8 |  | 2 | AI
PY1105I | PY1105I | FILTER AIR BAG OF PRESSURE #9 | FTP-1 | POTLINE | BAG HOUSE | REAL | KPA | Yes | 0.4 | 0.6 | 0.3 | 0.15 |  | 192.168.1.11 |  | ControlLogix | FILTER-9 | PRESSURE #9 |  | 2 | AI
PY1105J | PY1105J | FILTER AIR BAG OF PRESSURE #10 | FTP-1 | POTLINE | BAG HOUSE | REAL | KPA | Yes | 0.4 | 0.6 | 0.3 | 0.15 |  | 192.168.1.11 |  | ControlLogix | FILTER-10 | PRESSURE #10 |  | 2 | AI
TY1101A | TY1101A | 1# ID FAN FRONT BEARING TEMPERATURE | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 65 | 70 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-1 | FAN FRONT BEARING TEMPERATURE |  | 1 | AI
TY1101B | TY1101B | 1# ID FAN REAR BEARING TEMPERATURE | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 65 | 70 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-1 | FAN REAR BEARING TEMPERATURE |  | 1 | AI
TY1101C | TY1101C | 1# ID FAN MOTOR FRONT BEARING TEMPERATURE | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 65 | 70 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-1 | MOTOR FRONT BEARING TEMPERATURE |  | 1 | AI
TY1101D | TY1101D | 1# ID FAN MOTOR REAR BEARING TEMPERATURE | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 65 | 70 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-1 | MOTOR REAR BEARING TEMPERATURE |  | 1 | AI
TY1101E | TY1101E | 1# ID FAN MOTOR Winding temperature A | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 120 | 125 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-1 | MOTOR Winding temperature A |  | 1 | AI
TY1101F | TY1101F | 1# ID FAN MOTOR Winding temperature B | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 120 | 125 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-1 | MOTOR Winding temperature B |  | 1 | AI
TY1101G | TY1101G | 1# ID FAN MOTOR Winding temperature C | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 120 | 125 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-1 | MOTOR Winding temperature C |  | 1 | AI
TY1101H | TY1101H | 1# ID FAN INLET TEMPERATURE | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 120 | 140 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-1 | INLET TEMPERATURE |  | 1 | AI
TY1102A | TY1102A | 2# ID FAN FRONT BEARING TEMPERATURE | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 65 | 70 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-2 | FAN FRONT BEARING TEMPERATURE |  | 1 | AI
TY1102B | TY1102B | 2# ID FAN REAR BEARING TEMPERATURE | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 65 | 70 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-2 | FAN REAR BEARING TEMPERATURE |  | 1 | AI
TY1102C | TY1102C | 2# ID FAN MOTOR FRONT BEARING TEMPERATURE | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 65 | 70 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-2 | MOTOR FRONT BEARING TEMPERATURE |  | 1 | AI
TY1102D | TY1102D | 2# ID FAN MOTOR REAR BEARING TEMPERATURE | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 65 | 70 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-2 | MOTOR REAR BEARING TEMPERATURE |  | 1 | AI
TY1102E | TY1102E | 2# ID FAN MOTOR Winding temperature A | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 120 | 125 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-2 | MOTOR Winding temperature A |  | 1 | AI
TY1102F | TY1102F | 2# ID FAN MOTOR Winding temperature B | FTP-1 | POTLINE | ID FAN | DINT | °C | Yes | 120 | 125 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-2 | MOTOR Winding temperature B |  | 1 | AI
TY1102G | TY1102G | 2# ID FAN MOTOR Winding temperature C | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 120 | 125 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-2 | MOTOR Winding temperature C |  | 1 | AI
TY1102H | TY1102H | 2# ID FAN INLET TEMPERATURE | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 120 | 140 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-2 | INLET TEMPERATURE |  | 1 | AI
TY1103A | TY1103A | 3# ID FAN FRONT BEARING TEMPERATURE | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 65 | 70 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-3 | FAN FRONT BEARING TEMPERATURE |  | 1 | AI
TY1103B | TY1103B | 3# ID FAN REAR BEARING TEMPERATURE | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 65 | 70 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-3 | FAN REAR BEARING TEMPERATURE |  | 1 | AI
TY1103C | TY1103C | 3# ID FAN MOTOR FRONT BEARING TEMPERATURE | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 65 | 70 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-3 | MOTOR FRONT BEARING TEMPERATURE |  | 1 | AI
TY1103D | TY1103D | 3# ID FAN MOTOR REAR BEARING TEMPERATURE | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 65 | 70 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-3 | MOTOR REAR BEARING TEMPERATURE |  | 1 | AI
TY1103E | TY1103E | 3# ID FAN MOTOR Winding temperature A | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 120 | 125 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-3 | MOTOR Winding temperature A |  | 1 | AI
TY1103F | TY1103F | 3# ID FAN MOTOR Winding temperature B | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 120 | 125 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-3 | MOTOR Winding temperature B |  | 1 | AI
TY1103G | TY1103G | 3# ID FAN MOTOR Winding temperature C | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 120 | 125 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-3 | MOTOR Winding temperature C |  | 1 | AI
TY1103H | TY1103H | 3# ID FAN INLET TEMPERATURE | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 120 | 140 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-3 | INLET TEMPERATURE |  | 1 | AI
TY1104A | TY1104A | 4# ID FAN FRONT BEARING TEMPERATURE | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 65 | 70 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-4 | FAN FRONT BEARING TEMPERATURE |  | 1 | AI
TY1104B | TY1104B | 4# ID FAN REAR BEARING TEMPERATURE | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 65 | 70 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-4 | FAN REAR BEARING TEMPERATURE |  | 1 | AI
TY1104C | TY1104C | 4# ID FAN MOTOR FRONT BEARING TEMPERATURE | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 65 | 70 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-4 | MOTOR FRONT BEARING TEMPERATURE |  | 1 | AI
TY1104D | TY1104D | 4# ID FAN MOTOR REAR BEARING TEMPERATURE | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 65 | 70 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-4 | MOTOR REAR BEARING TEMPERATURE |  | 1 | AI
TY1104E | TY1104E | 4# ID FAN MOTOR Winding temperature A | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 120 | 125 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-4 | MOTOR Winding temperature A |  | 1 | AI
TY1104F | TY1104F | 4# ID FAN MOTOR Winding temperature B | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 120 | 125 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-4 | MOTOR Winding temperature B |  | 1 | AI
TY1104G | TY1104G | 4# ID FAN MOTOR Winding temperature C | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 120 | 125 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-4 | MOTOR Winding temperature C |  | 1 | AI
TY1104H | TY1104H | 4# ID FAN INLET TEMPERATURE | FTP-1 | POTLINE | ID FAN | REAL | °C | Yes | 120 | 140 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-4 | INLET TEMPERATURE |  | 1 | AI
IYAN1101 | IYAN1101 | ID FAN CURRENT #1 | FTP-1 | POTLINE | ID FAN | REAL | Amp | Yes | 42 | 46.5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-1 | CURRENT |  | 1 | AI
IYAN1102 | IYAN1102 | ID FAN CURRENT #2 | FTP-1 | POTLINE | ID FAN | REAL | Amp | Yes | 42 | 46.5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-2 | CURRENT |  | 1 | AI
IYAN1103 | IYAN1103 | ID FAN CURRENT #3 | FTP-1 | POTLINE | ID FAN | REAL | Amp | Yes | 42 | 46.5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-3 | CURRENT |  | 1 | AI
IYAN1104 | IYAN1104 | ID FAN CURRENT #4 | FTP-1 | POTLINE | ID FAN | REAL | Amp | Yes | 42 | 46.5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-4 | CURRENT |  | 1 | AI
IYFBR1101 | IYFBR1101 | ROOTS FAN CURRENT #1 | FTP-1 | POTLINE | BLOWER | REAL | Amp | Yes | 70 | 94 |  |  |  | 192.168.1.11 |  | ControlLogix | AIR ROOT BLOWER-1 | CURRENT |  | 2 | AI
IYFBR1102 | IYFBR1102 | ROOTS FAN CURRENT #2 | FTP-1 | POTLINE | BLOWER | REAL | Amp | Yes | 70 | 94 |  |  |  | 192.168.1.11 |  | ControlLogix | AIR ROOT BLOWER-2 | CURRENT |  | 2 | AI
IYFBC1101 | IYFBC1101 | HIGHT PRESSURE CENTRIFUGAL VENTILATOR #1 | FTP-1 | POTLINE | FAN | REAL | Amp | Yes | 50 | 75 |  |  |  | 192.168.1.11 |  | ControlLogix | AIRSLIDE FAN-1 | PRESSURE-1 |  | 2 | AI
IYFBC1102 | IYFBC1102 | HIGHT PRESSURE CENTRIFUGAL VENTILATOR #2 | FTP-1 | POTLINE | FAN | REAL | Amp | Yes | 50 | 75 |  |  |  | 192.168.1.11 |  | ControlLogix | AIRSLIDE FAN-2 | PRESSURE-2 |  | 2 | AI
HZ1101A | HZ1101A | ID FAN VALVE OF DEGREE (DAMPER FEEDBACK) #1 | FTP-1 | POTLINE | ID FAN | REAL | % | [6 empty] | 192.168.1.11 |  | ControlLogix | ID FAN-1 | DAMPER-1 |  | 1 | AI
HZ1102A | HZ1102A | ID FAN VALVE OF DEGREE (DAMPER FEEDBACK) #2 | FTP-1 | POTLINE | ID FAN | REAL | % | [6 empty] | 192.168.1.11 |  | ControlLogix | ID FAN-2 | DAMPER-2 |  | 1 | AI
HZ1103A | HZ1103A | ID FAN VALVE OF DEGREE (DAMPER FEEDBACK) #3 | FTP-1 | POTLINE | ID FAN | REAL | % | [6 empty] | 192.168.1.11 |  | ControlLogix | ID FAN-3 | DAMPER-3 |  | 1 | AI
HZ1104A | HZ1104A | ID FAN VALVE OF DEGREE (DAMPER FEEDBACK) #4 | FTP-1 | POTLINE | ID FAN | REAL | % | [6 empty] | 192.168.1.11 |  | ControlLogix | ID FAN-4 | DAMPER-4 |  | 1 | AI
AY1101 | AY1101 | FTP-1 DUST ANALYZER | FTP-1 | POTLINE | STACK | REAL | mg/m3 | Yes | 5 | 10 |  |  |  | 192.168.1.11 |  | ControlLogix | DUST ANALYZER | PM VALUE FROM STACK |  | 2 | AI
AY1102 | AY1102 | FTP-1 HF ANALYZER | FTP-1 | POTLINE | STACK | REAL | mg/m3 | Yes | 0.35 | 0.45 |  |  |  | 192.168.1.11 |  | ControlLogix | HF ANALYZER | HF VALUE FROM STACK |  | 2 | AI
TY1105A | TY1105A | FILTER INLET TEMPERATURE #1 | FTP-1 | POTLINE | DUCT | REAL | °C | Yes | 120 | 140 |  |  |  | 192.168.1.11 |  | ControlLogix | DUCT INLET-1 | TEMPERATURE-1 |  | 2 | AI
TY1105B | TY1105B | FILTER INLET TEMPERATURE #2 | FTP-1 | POTLINE | DUCT | REAL | °C | Yes | 120 | 140 |  |  |  | 192.168.1.11 |  | ControlLogix | DUCT INLET-2 | TEMPERATURE-2 |  | 2 | AI
PDY1101 | PDY1101 | FILTER INLET OUTLET PRESSURE #1 | FTP-1 | POTLINE | BAG HOUSE | REAL | KPA | Yes | 2.2 | 3 | 0.8 | 0.5 |  | 192.168.1.11 |  | ControlLogix | FILTER-1 | PRESSURE-1 |  | 2 | AI
PDY1102 | PDY1102 | FILTER INLET OUTLET PRESSURE #2 | FTP-1 | POTLINE | BAG HOUSE | REAL | KPA | Yes | 2.2 | 3 | 0.8 | 0.5 |  | 192.168.1.11 |  | ControlLogix | FILTER-2 | PRESSURE-2 |  | 2 | AI
PDY1104 | PDY1104 | FILTER INLET OUTLET PRESSURE #4 | FTP-1 | POTLINE | BAG HOUSE | REAL | KPA | Yes | 2.2 | 3 | 0.8 | 0.5 |  | 192.168.1.11 |  | ControlLogix | FILTER-4 | PRESSURE-4 |  | 2 | AI
PDY1105 | PDY1105 | FILTER INLET OUTLET PRESSURE #5 | FTP-1 | POTLINE | BAG HOUSE | REAL | KPA | Yes | 2.2 | 3 | 0.8 | 0.5 |  | 192.168.1.11 |  | ControlLogix | FILTER-5 | PRESSURE-5 |  | 2 | AI
PDY1106A | PDY1106A | FILTER INLET OUTLET PRESSURE #6 | FTP-1 | POTLINE | BAG HOUSE | REAL | KPA | Yes | 2.2 | 3 | 0.8 | 0.5 |  | 192.168.1.11 |  | ControlLogix | FILTER-6 | PRESSURE-6 |  | 2 | AI
PDY1107A | PDY1107A | FILTER INLET OUTLET PRESSURE #7 | FTP-1 | POTLINE | BAG HOUSE | REAL | KPA | Yes | 2.2 | 3 | 0.8 | 0.5 |  | 192.168.1.11 |  | ControlLogix | FILTER-7 | PRESSURE-7 |  | 2 | AI
PDY1108 | PDY1108 | FILTER INLET OUTLET PRESSURE #8 | FTP-1 | POTLINE | BAG HOUSE | REAL | KPA | Yes | 2.2 | 3 | 0.8 | 0.5 |  | 192.168.1.11 |  | ControlLogix | FILTER-8 | PRESSURE-8 |  | 2 | AI
PDY1109 | PDY1109 | FILTER INLET OUTLET PRESSURE #9 | FTP-1 | POTLINE | BAG HOUSE | REAL | KPA | Yes | 2.2 | 3 | 0.8 | 0.5 |  | 192.168.1.11 |  | ControlLogix | FILTER-9 | PRESSURE-9 |  | 2 | AI
PDY1110 | PDY1110 | FILTER INLET OUTLET PRESSURE #10 | FTP-1 | POTLINE | BAG HOUSE | REAL | KPA | Yes | 2.2 | 3 | 0.8 | 0.5 |  | 192.168.1.11 |  | ControlLogix | FILTER-10 | PRESSURE-10 |  | 2 | AI
FY1100 | FY1100 | OUTLET FLOW | FTP-1 | POTLINE | BAG HOUSE | REAL | Nm3/Hr | Yes | 1200000 | 1500000 | 700000 |  |  | 192.168.1.11 |  | ControlLogix | OUTLET DUCT | FLOW |  | 5 | AI
VYAN1101A | VYAN1101A | ID FAN FRONT BEARING X VIBRATION #1 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-1 | FAN FRONT BEARING X VIBRATION #1 |  | 1 | AI
VYAN1101B | VYAN1101B | ID FAN FRONT BEARING Y VIBRATION #1 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-1 | FAN FRONT BEARING Y VIBRATION #1 |  | 1 | AI
VYAN1101C | VYAN1101C | ID FAN REAR BEARING X VIBRATION #1 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-1 | FAN REAR BEARING X VIBRATION #1 |  | 1 | AI
VYAN1101D | VYAN1101D | ID FAN REAR BEARING Y VIBRATION #1 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-1 | FAN REAR BEARING Y VIBRATION #1 |  | 1 | AI
VYAN1102A | VYAN1102A | ID FAN FRONT BEARING X VIBRATION #2 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-2 | FAN FRONT BEARING X VIBRATION #2 |  | 1 | AI
VYAN1102B | VYAN1102B | ID FAN FRONT BEARING Y VIBRATION #2 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-2 | FAN FRONT BEARING Y VIBRATION #2 |  | 1 | AI
VYAN1102C | VYAN1102C | ID FAN REAR BEARING X VIBRATION #2 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-2 | FAN REAR BEARING X VIBRATION #2 |  | 1 | AI
VYAN1102D | VYAN1102D | ID FAN REAR BEARING Y VIBRATION #2 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-2 | FAN REAR BEARING Y VIBRATION #2 |  | 1 | AI
VYAN1103A | VYAN1103A | ID FAN FRONT BEARING X VIBRATION #3 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-3 | FAN FRONT BEARING X VIBRATION #3 |  | 1 | AI
VYAN1103B | VYAN1103B | ID FAN FRONT BEARING Y VIBRATION #3 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-3 | FAN FRONT BEARING Y VIBRATION #3 |  | 1 | AI
VYAN1103C | VYAN1103C | ID FAN REAR BEARING X VIBRATION #3 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-3 | FAN REAR BEARING X VIBRATION #3 |  | 1 | AI
VYAN1103D | VYAN1103D | ID FAN REAR BEARING Y VIBRATION #3 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-3 | FAN REAR BEARING Y VIBRATION #3 |  | 1 | AI
VYAN1104A | VYAN1104A | ID FAN FRONT BEARING X VIBRATION #4 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-4 | FAN FRONT BEARING X VIBRATION #4 |  | 1 | AI
VYAN1104B | VYAN1104B | ID FAN FRONT BEARING Y VIBRATION #4 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-4 | FAN FRONT BEARING Y VIBRATION #4 |  | 1 | AI
VYAN1104C | VYAN1104C | ID FAN REAR BEARING X VIBRATION #4 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-4 | FAN REAR BEARING X VIBRATION #4 |  | 1 | AI
VYAN1104D | VYAN1104D | ID FAN REAR BEARING Y VIBRATION #4 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-4 | FAN REAR BEARING Y VIBRATION #4 |  | 1 | AI
PY1102A | PY1102A | ID FAN INLET PRESSURE #1 | FTP-1 | POTLINE | ID FAN | REAL | KPA | Yes | 3 | 3.5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-1 | INLET PRESSURE #1 |  | 1 | AI
PY1102B | PY1102B | ID FAN INLET PRESSURE #2 | FTP-1 | POTLINE | ID FAN | REAL | KPA | Yes | 3 | 3.5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-2 | INLET PRESSURE #2 |  | 1 | AI
PY1102C | PY1102C | ID FAN INLET PRESSURE #3 | FTP-1 | POTLINE | ID FAN | REAL | KPA | Yes | 3 | 3.5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-3 | INLET PRESSURE #3 |  | 1 | AI
PY1102D | PY1102D | ID FAN INLET PRESSURE #4 | FTP-1 | POTLINE | ID FAN | REAL | KPA | Yes | 3 | 3.5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-4 | INLET PRESSURE #4 |  | 1 | AI
LY3101 | LY3101 | CYCLE TANK LEVEL DETECTE | FTP-1 | POTLINE | COOLING STATION | REAL | M | Yes | 4 | 5 | 2.5 | 2 |  | 192.168.1.11 |  | ControlLogix | COOLING TANK | LEVEL IN METER |  | 1 | AI
PY3101 | PY3101 | CYCLE OUTLET PIPE PRESSURE | FTP-1 | POTLINE | COOLING STATION | REAL | KPA | Yes | 2 | 3 | 0.7 | 0.5 |  | 192.168.1.11 |  | ControlLogix | OUTLET COOLING LINE | PRESSURE |  | 1 | AI
LY1101 | LY1101 | FRESH ALUMINA CANBIN LEVEL | FTP-1 | POTLINE | PRIMARY SILO | REAL | M | Yes | 16 | 17.5 |  |  |  | 192.168.1.11 |  | ControlLogix | FRESH ALUMINA | LEVEL IN METER |  | 3 | AI
LY1102 | LY1102 | ENRICH ALUMINA CABIN LEVEL | FTP-1 | POTLINE | ENRICH SILO | REAL | M | Yes | 12 | 14 |  |  |  | 192.168.1.11 |  | ControlLogix | ENRICH ALUMINA | LEVEL IN METER |  | 3 | AI
FY3101 | FY3101 | CYCLE OUTLET PIPE FLOW METER | FTP-1 | POTLINE | COOLING STATION | REAL | m3/h | Yes | 30 | 35 |  |  |  | 192.168.1.11 |  | ControlLogix | OUTLET COOLING LINE | FLOW |  | 1 | AI
VY1101A | VY1101A | FRONT VALVE DEGREE OF DESSLAGGING | FTP-1 | POTLINE | PRIMARY SILO | REAL | % | [6 empty] | 192.168.1.11 |  | ControlLogix | FRESH ALUMINA FEEDING | % |  | 3 | AI
FY1101 | FY1101 | FRESH ALUMINA FLOW | FTP-1 | POTLINE | PRIMARY SILO | REAL | Ton/h | Yes | 30 |  | 10 | 8 |  | 192.168.1.11 |  | ControlLogix | FRESH ALUMINA FEEDING | FLOW |  | 3 | AI
CV1101 | CV1101 | FRENQUENCE OF Fresh alumina silo bottom screw conveyor | FTP-1 | POTLINE | PRIMARY SILO | REAL | Hz | [6 empty] | 192.168.1.11 |  | ControlLogix | FRESH ALUMINA FEEDING | Hz |  | 3 | AI
TY3101 | TY3101 | CYCLE WATER OUTLET TEMPERATURE | FTP-1 | POTLINE | COOLING STATION | REAL | °C | Yes | 40 | 50 |  |  |  | 192.168.1.11 |  | ControlLogix | OUTLET COOLING LINE | TEMPERATURE |  | 1 | AI
VYAN1101E | VYAN1101E | ID FAN MOTOR FRONT BEARING X VIBRATION #1 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-1 | MOTOR FRONT BEARING X VIBRATION #1 |  | 1 | AI
VYAN1101F | VYAN1101F | ID FAN MOTOR FRONT BEARING Y VIBRATION #1 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-1 | MOTOR FRONT BEARING Y VIBRATION #1 |  | 1 | AI
VYAN1101G | VYAN1101G | ID FAN MOTOR REAR BEARING X VIBRATION #1 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-1 | MOTOR REAR BEARING X VIBRATION #1 |  | 1 | AI
VYAN1101H | VYAN1101H | ID FAN MOTOR REAR BEARING Y VIBRATION #1 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-1 | MOTOR REAR BEARING Y VIBRATION #1 |  | 1 | AI
VYAN1102E | VYAN1102E | ID FAN MOTOR FRONT BEARING X VIBRATION #2 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-2 | MOTOR FRONT BEARING X VIBRATION #2 |  | 1 | AI
VYAN1102F | VYAN1102F | ID FAN MOTOR FRONT BEARING Y VIBRATION #2 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-2 | MOTOR FRONT BEARING Y VIBRATION #2 |  | 1 | AI
VYAN1102G | VYAN1102G | ID FAN MOTOR REAR BEARING X VIBRATION #2 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-2 | MOTOR REAR BEARING X VIBRATION #2 |  | 1 | AI
VYAN1102H | VYAN1102H | ID FAN MOTOR REAR BEARING Y VIBRATION #2 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-2 | MOTOR REAR BEARING Y VIBRATION #2 |  | 1 | AI
VYAN1103E | VYAN1103E | ID FAN MOTOR FRONT BEARING X VIBRATION #3 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-3 | MOTOR FRONT BEARING X VIBRATION #3 |  | 1 | AI
VYAN1103F | VYAN1103F | ID FAN MOTOR FRONT BEARING Y VIBRATION #3 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-3 | MOTOR FRONT BEARING Y VIBRATION #3 |  | 1 | AI
VYAN1103G | VYAN1103G | ID FAN MOTOR REAR BEARING X VIBRATION #3 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-3 | MOTOR REAR BEARING X VIBRATION #3 |  | 1 | AI
VYAN1103H | VYAN1103H | ID FAN MOTOR REAR BEARING Y VIBRATION #3 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-3 | MOTOR REAR BEARING Y VIBRATION #3 |  | 1 | AI
VYAN1104E | VYAN1104E | ID FAN MOTOR FRONT BEARING X VIBRATION #4 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-4 | MOTOR FRONT BEARING X VIBRATION #4 |  | 1 | AI
VYAN1104F | VYAN1104F | ID FAN MOTOR FRONT BEARING Y VIBRATION #4 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-4 | MOTOR FRONT BEARING Y VIBRATION #4 |  | 1 | AI
VYAN1104G | VYAN1104G | ID FAN MOTOR REAR BEARING X VIBRATION #4 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-4 | MOTOR REAR BEARING X VIBRATION #4 |  | 1 | AI
VYAN1104H | VYAN1104H | ID FAN MOTOR REAR BEARING Y VIBRATION #4 | FTP-1 | POTLINE | ID FAN | REAL | mm/s | Yes | 3.5 | 5 |  |  |  | 192.168.1.11 |  | ControlLogix | ID FAN-4 | MOTOR REAR BEARING Y VIBRATION #4 |  | 1 | AI
MV1101A | MV1101A | Feedback of the regulating damper for cold air valve No.1 of the main flue | FTP-1 | POTLINE | INLET DUCT | REAL | % | [6 empty] | 192.168.1.11 |  | ControlLogix | DILUTION DAMPER-1 | % |  | 4 | AI
MV1102A | MV1102A | Feedback of the regulating damper for cold air valve No.2 of the main flue | FTP-1 | POTLINE | INLET DUCT | REAL | % | [6 empty] | 192.168.1.11 |  | ControlLogix | DILUTION DAMPER-2 | % |  | 4 | AI
HZ1101B | HZ1101B | ID FAN REGULAR VALVE COMMAND #1 | FTP-1 | POTLINE | ID FAN | REAL | % | [6 empty] | 192.168.1.11 |  | ControlLogix | ID FAN-1 | % |  | 1 | AO
HZ1102B | HZ1102B | ID FAN REGULAR VALVE COMMAND #2 | FTP-1 | POTLINE | ID FAN | REAL | % | [6 empty] | 192.168.1.11 |  | ControlLogix | ID FAN-2 | % |  | 1 | AO
HZ1103B | HZ1103B | ID FAN REGULAR VALVE COMMAND #3 | FTP-1 | POTLINE | ID FAN | REAL | % | [6 empty] | 192.168.1.11 |  | ControlLogix | ID FAN-3 | % |  | 1 | AO
HZ1104B | HZ1104B | ID FAN REGULAR VALVE COMMAND #4 | FTP-1 | POTLINE | ID FAN | REAL | % | [6 empty] | 192.168.1.11 |  | ControlLogix | ID FAN-4 | % |  | 1 | AO
VT1101B | VT1101B | SETPOINT OF THE FRESH STORAGE TANK REGULATING VALVE | FTP-1 | POTLINE | PRIMARY SILO | REAL | % | [6 empty] | 192.168.1.11 |  | ControlLogix | FRESH ALUMINA FEEDING | % |  | 3 | AO
CV1101B | CV1101B | SETPOINT OF Fresh alumina silo bottom screw conveyor | FTP-1 | POTLINE | PRIMARY SILO | REAL | Hz | [6 empty] | 192.168.1.11 |  | ControlLogix | FRESH ALUMINA FEEDING | Hz |  | 3 | AO
Fresh_SILO_MT | Fresh_SILO_MT | PRIMARY SILO LEVEL IN MT | FTP-1 | POTLINE | PRIMARY SILO | REAL | MT | Yes | 3200 | 3500 | [6 empty] | FRESH ALUMINA | LEVEL IN MT |  | 3
Enrich_SILO_MT | Enrich_SILO_MT | ENRICH SILO LEVEL IN MT | FTP-1 | POTLINE | ENRICH SILO | REAL | MT | Yes | 2000 | 2500 | [6 empty] | ENRICH ALUMINA | LEVEL IN MT |  | 3

## PLC DETAILS
S.NO | Item | Description | DETAILS
1 | PLC Manufacturer | Controller vendor | ROCKWELL
2 | PLC Model | CPU model | 1756-L71
3 | Programming Software | Engineering software | STUDIO-5000
4 | Software Version | Installed version | V33
5 | Backup File | Latest source backup with comments
6 | IP ADDRESS |  | 192.168.1.11
7 | SUB NET MASK |  | 255.255.255.0
8 | SWITCH DETAILS |  | UN MANAGED
9 | Protocol | Communication protocol | EtherNet/IP
10 | SCADA SOFTWARE | FACTORY TALK VIEW STUDIO
11 | Software Version | Installed version | V11

## Shift Data
Shift Name | Start time | End Time
Shift-A | 5:00 | 13:00
Shift-B | 13:00 | 21:00
Shift-C | 21:00 | 5:00

## User Roles
User Roles | Alarm Seen | Alarm Ack | Alarm Cleared | ALARM CHANGED | ALARM ADDITION | Tag Enabled
Admin | Yes | Yes | Yes | YES | YES | YES
OPRATOR | Yes | Yes | NO | NO | NO | YES

## Reports
Serial No. | Tag Id | Report Type | Tag Enabled
1 | 32322 | Daily | Yes